Specification Sheet

Lake Cable Part #: V1011427(1)/X-LADOT

Description:	10 AWG 1 conductor + 14 AWG 27 conductor solid bare copper with PVC/Nylon insulation, unshielded with an overall PVC jacket 600V control tray cable, approved for use in SUN RES DIR BUR 75°C applications.

Element 1 Your signature constitutes that you have read and agreed to this specification sheet and upon confirmation of your order; this item may be non-cancelable and non-returnable.

| Signature Company Date |  |
| --- | --- |

- Conductor (First Element)

  - AWG Size & Stranding:	10 AWG Solid

  - Material:		Annealed Bare Copper

  - Conductor Count:	1 Conductors

- Insulation

  - Material:		Polyvinylchloride & Nylon

  - Wall Thickness:	0.022” PVC & 0.008” Nylon

  - Color Code:		White

  - Legend Type:	Conductor shall be permanently identified via surface inkjet print

  - Legend:	E206524 10AWG (UL) TYPE THHN OR THWN 600V 75C WET OR DRY GASOLINE AND OIL RESISTANT II    VW-1    "ROHS COMPLIANT"    MADE IN USA

Element 2

- Conductor (Second Element)

  - AWG Size & Stranding:	14 AWG Solid

  - Material:		Annealed Bare Copper

  - Conductor Count:	27 Conductors

- Insulation

  - Material:		Polyvinylchloride & Nylon

  - Wall Thickness:	0.016” PVC & 0.005” Nylon

  - Color Code:	Brown/Orange, Yellow/Orange, Red/Orange, Yellow/Black, Brown/Black, Red/Black, Red/Purple/Purple, Brown/Purple/Purple, Blue/Black, Blue/Orange, Red/Gray, Blue/Purple, White/Black, Black/Red, Black, Blue/Gray, Red/Orange/Orange, Brown/Black/Black, Red/Black/Black, Brown/Purple, Yellow/Purple, Red/Purple, Brown/Gray, Yellow/Gray, Brown/Orange/Orange, Red/Gray/Gray, Brown/Gray/Gray (All stripes are spiraled)

  - Legend:	E206524 14AWG (UL) TYPE THHN OR THWN 600V 75C WET OR DRY GASOLINE AND OIL RESISTANT II    VW-1    "ROHS COMPLIANT"    MADE IN USA

- Overall Assembly

  - Fillers:			N/A

  - Binder:			Clear Mylar

- Jacket

  - Material:		Polyvinylchloride

  - Wall Thickness:	0.080”

  - Diameter:		0.851” +/- 0.070”

  - Color:			Black

  - Ripcord:		Yes

  - Weight:		644 lbs./Mft.

- Markings

  - Type:			Cable shall be permanently identified via surface inkjet print

  - Legend:	LAKE CABLE THWN 27/C #14 AWG 1/C #10 AWG 600V   "ROHS COMPLIANT"   MADE IN USA

  - Footage Markers:	Yes

Specification Sheet

Lake Cable Part #: V1011427(1)/X-LADOT

- Standards

  - Suitable for Direct Burial and Sunlight Resistant applications

  - Jacket meets IMSA 19-1

  - Cable meets RoHS 2002/95/EC Directive, RoHS 2 2011/65/EU Directive, RoHS 3 2015/863/EU Directive

  - Cable is REACH compliant per Regulation (EC) No 1907/2006 (224) Updated June 10, 2022

  - Made in the USA

  - WARNING: This product may contain chemicals, such as Vinyl Chloride, known to the state of California to cause birth defects or other reproductive harm. For more information, go to www.P65Warnings.ca.gov.    Wash hands after handling

ALL SPECIFIED PARAMETERS WITHOUT A TOLERANCE ARE NOMINAL AND SUBJECT TO VERIFICATION. LAKE CABLE IS NOT RESPONSIBLE FOR UNKNOWN PERFORMANCE ATTRIBUTES THAT WERE NOT MADE KNOWN TO LAKE CABLE AT THE TIME OF DESIGN.